Aeries

O N   T H E   B A Y

COMMON DEFICIENCIES

&

OPPORTUNITIES for IMPROVEMENT

The following deficiencies in design and construction and opportunities for improvement have been found or are suspected to exist in multiple units as they were originally built.

Common Deficiencies

Following items are costly to repair or are safety hazards:

1.  Attachment of decks -- not flashed properly to keep out water.  Look for water stains on walls and ceilings – particularly below patio doors, moisture damaged framing in walls below the decks and, moisture-damaged subfloor in front of second floor of patio doors.

Remedies:  Install gutters above decks with downspouts extended to remove water from foundations.  Install flashing, which may be done without removing decks.  However, decks must be removed to repair damaged framing inside the walls below decks.  Reinstall patio doors above the first floor in prefabricated drain pans.

2.  Corroded joist hangers under decks in combination with lack of toenails can be serious safety hazards.

Remedy:  Replace with hot dip galvanized or stainless steel hangers and fasteners, nailed properly.

3.  Thoroughly rotten framing has been found inside hollow box columns at outside corners of front and rear decks of detached houses.  Attachments of the decks were not flashed to keep water out; framing is not pressure treated; and, there is no ventilation to allow drying or inspection inside the boxes.

Remedy:  Replace framing as originally built but with proper flashing.  Alternatively, replace the box with a 6x6 pressure treated wood post or 3” diameter iron pipe with top and bottom steel plates – hot dipped galvanized.

4.  Split, sagging framing at the outside corners of decks of townhouses.

Remedies:  Jack-up decks to install posts from the patio or from footings of the concrete block walls.

5.  Rusty nails in trellis frames fail unexpectedly -- in front of townhouses.

Remedy:  Replace framing with pressure treated lumber.  Some new treatment chemicals are very corrosive to steel.  Use stainless steel fasteners.

6.  Severe deterioration of stucco finishes on concrete block walls often accompanied by crumbling mortar joints, which is caused by excessive moisture inside the block voids with no ventilation to allow drying and to relieve vapor pressure in extreme hot and cold conditions.

Remedies:  Install gutters with downspouts extended to remove water from the foundation; install 1” diameter vinyl vents in block voids near the bottom and top of the walls; remove loose coatings including mortar parging and deteriorated mortar joints; “parge” flat tops of walls to drain; repair mortar and refinish.

7.  Failed fire retardant treated plywood decking under roofing along adjacent townhouses is a faulty product, which is no longer manufactured.  The material lost structural character after approximately eight years.  Some townhouses were reroofed without replacing this material or without installing alternative fire protection.  Look for dark color and damage from being nailed or walked on.  Deteriorated/damaged FRT will not hold nails and is not safe to walk on.

Remedy:  When reroofing, replace FRT with new, approved fire retardant materials such as Blazeguard or 5/8” Type X gypsum underlayment; obtain a building permit and final inspection by a City Building Inspector.

8.   Flanged plexiglass skylight bubbles become darkened, stained and/or leak.

Remedies:  Replace with curb mounted, flat insulated glass units w/ low-e coating and proper flashing securely fastening to the roof deck.  Allow 1” drainage channel all around and install water diverter flashing above each skylight.

9.  Aluminum frame windows and patio door insulated glass units (IGUs) fog. Fogging in is due to failure of the seals, which allows moisture between the panes.  To correct this, IGUs or windows must be replaced.  In the initial stages, fogging may be apparent only in some weather conditions.

Remedy:  The best warranties for replacement IGUs are 5-years.  If windows are replaced, choose energy efficient units including thermal breaks in frames and

low–e coating on windows with solar exposure.  Twenty-year and lifetime warranties from fogging are available with replacement windows.

10.  “Big Blue”polybutylene water lines develop leaks between meters and copper pipe in townhouses and single-family houses.  Connections are under or between driveways. This material is no longer manufactured.  Monitor water usage.  Look for steady increases without cause.  Usage should not exceed 100 gallons per day per person.  Half that amount is reasonable without watering grass or washing autos and with modest conservation.

Remedy:  Replace with polyethylene, PEX or copper pipe.

11.  Dryer ducts are not installed straight with well-sealed joints.  When a hole was cut in floor of the L.R. of our townhouse on the side opposite from the laundry room below, hot air and lint blew out.  Accumulating lint is a fire hazard and excessive moisture may create mold between floor and ceiling.

Remedy:  Replace duct with straight, well-sealed metal pipe.  This may require making holes in L.R. floor for access to replace pipe.

12.  Recirculating stove hoods should be sealed.  Our stove hood vented into the wall of the HVAC equipment closet.  When the exhaust fan was operating, we could smell whatever was on the stove in the closet.  This was hazardous and unsanitary.

Remedy:  Convert to a recirculating stove vent hood.  However, charcoal filters are necessary and must be replaced every 6-9 month, depending on use.

13.  Wind scours attic insulation behind eaves of flat ceilings, leaving uninsulated sections of ceilings 3-4’ long between trusses or rafters.

Remedy:  Install “stops” to prevent insulation from filling eaves and “baffles” to preserve an air space below the roof sheathing for ventilation.  Then add insulation.  Cellulose is recommended because it seals air leakage better than loosefill fiberglass and it fills irregularities better than batts.  It is fire and insect retardant and it is a recycled product.

14.  Rotten siding and wall framing behind concrete block planters between corners of garages and stairs in townhouses with stairs at the front entries.  In a storm about five years ago, a portion of a garage wall on Hermit Thrush washed out and water from the roof flowed through the wall and out the garage door down the driveway.  These planters are also prime points of entry for subterranean termites.

Remedies:  Remove these concrete block “planters” altogether; or, cap and seal with flashing up the wall behind the siding and concrete sloped to drain away from the structure.  Many of these planters have been capped without flashing.

15.  Cedar shakes are short lived as installed with no air space between roof decking and the underside of the shakes.  This installation accelerates rotting, splitting and curling.

Remedy:  Replace shakes with architectural grade laminated shingles such as GAF Timberline 30 or CertainTeed Hatteras, which can be installed to 110 mph specifications.

16.  Wind rating is only 60 mph for 3-tab Royal Sovereign shingles specified for townhouses and there is now little cost difference between these and heavier laminated or architectural shingles.

Remedy:  Encourage the Civic League to maintain the color standard, but change the specification to higher wind rated shingles and installation.

Maintenance and Opportunities for Improvement

Following are suggestions for reduced maintenance, high wind resistance, improved energy efficiency and/or comfort, which are compatible with architectural standards of Aeries where this applies:

1.  Galvanized steel chimney chase covers and chimney caps rust.  In the Nov 2009 nor’easter, tops of many chimney caps blew off because spark arrester screens were severely corroded.

Remedies:  Apply rust converter to chimney chase covers, and flue pipes, then two applications of rust-resistant finish coat.

Replace spark arrester screens with stainless steel or replace entire caps with stainless steel caps.  However, caps used at Aeries are not standard.  Currently available caps require modification to preserve an air gap between the inner flue and outer liner with sufficient lap to minimize water entry (except in severe wind/rain).  Proper replacement requires more than most chimney professionals are able or willing to do.

Alternative: Remove chimney chase pipe and/or chimney flue and convert fireplaces to entertainment centers or to unvented propane gas logs.

2.  Subterranean termites have caused damage at Aeries ranging from ravaging a little- used garage door to destroying entire walls (in conjunction with moisture damage).

Remedy:  Maintain a Termite Protection Plan that includes annual inspection with a reputable company and encourage immediate neighbors to use the same company.

3.  Replace toilets w/ low-flow to reduce volume and cost of water and sewer.  Seventy-five dollar rebate for each toilet replaced is available from the City.  Find out more at www.vbgov.com/dpu or 385-4631.  The rebate is partially offset by the cost of permits.

4.  Replace recirculating bathroom fan filters regularly; or, replace recirculating fans with outside venting fans, which is easy for bathrooms with attic space above.

5.  Replace 2x12x12 wood pads used as “washers” for bolts supporting deck ledgers of townhouses.  Galvanized cast iron stars are a long-lived decorative alternative.

6.  Replace weathered cedar siding and deteriorated nails with 8.25” Cedarmill preprimed cement board siding, blind nailed with galvanized or stainless steel nails.

7.  Replace outside deck handrail balusters spaced no more than 4” apart for child safety as required in new construction inside and outside.

8.  Ground Fault Interrupter protection is recommended for all receptacles in proximity to water:  Kitchen, bathrooms, Garage and outside as required in new construction.

9.  Arc Fault Circuit Interrupters (AFCIs) for bedrooms and tamperproof receptacles throughout can be installed for additional safety as required in new construction.